## Slide 1: 2026 National Electrical Code (NEC) Changes
Itinerary
2026 NEC:
Chapter 1 General
Chapter 2 Wiring & protection
Electrical in the thermal envelope
2027 ICC Release dates
Next Session
chapter 3 wiring methods & materials (F
Chapter 4 equipment for general use
chapter 5 specific occupancies & locations

## Slide 2: 2026 National Electrical Code (NEC) Changes
Article 100 Energy Storage System
Definition revised
One or more devises, capable of storing energy for us at a later time, that are assembled together.
2023 NEC, Art 480.2 Storage Battery:
A single or group or rechargeable cells connected-together electrically in series, in parallel, or a combination of both, and comprised of lead-acid, nickel-cadmium or other rechargeable electrochemical types.
2023 NEC, Art 706.2 Energy Storage System (ESS):
One or components assembled-together capable of storing energy and providing electrical energy into the premises wiring system or an electric power production and distribution network.
When is a battery an ESS?
When the manufacturer assembles it together and tested and listed as an ESS under UL ?.
UL 9540

## Slide 3: 2026 National Electrical Code (NEC) Changes
Article 100 Energy Storage System
Definition of revised
One or more devises, capable of storing energy for us at a later time, that are assembled together.
Info Note 1: An ESS can include batteries, kinetic devices like a flywheel or compressed air, or capacitors.
Info Note 2: A stationary battery system is not an ESS because an ESS is listed as a complete system. It can include inverters, charge controllers, and similar.

## Slide 4: 2026 National Electrical Code (NEC) Changes
Battery
ESS
≠
Are they equal?
NOT tested and listed as an ESS

## Slide 5: 2026 National Electrical Code (NEC) Changes
SB1202 & ESS

## Slide 6: 2026 National Electrical Code (NEC) Changes
SB1202 & ESS

## Slide 7: 2026 National Electrical Code (NEC) Changes
Squirrel
2024 IMC 304.3
Equipment and appliances having an ignition source and located in hazardous locations and…private garages…shall be elevated 18” above the floor…
Exception: …not required for appliances that are listed as flammable vapor ignition resistant. (FVIR)
ESS is not an appliance regulated by the IMC but is equipment is a component permanently installed and integrated to control environmental conditions.
Control is a manual or automatic devise designed to regulate the…electrical supply to…a mechanical system.
Does an ESS need to be elevated in a garage?

## Slide 8: 2026 National Electrical Code (NEC) Changes
Article 100 Metering Center
Definition is NEW
A panelboard in an enclosure that also contains one or more meter sockets.
A panelboard is a single or a group of panel units designed for assembly in the form as a single panel, including buses and automatic overcurrent devices…

## Slide 9: 2026 National Electrical Code (NEC) Changes
Article 100 Pool
Definition is revised
Equipment designed to contain water for swimming, recreation, wading, or therapeutic use.
2023 NEC, Art 680.2 Pool: Manufactured or field-constructed equipment designed to contain water on a permanent basis and used for swimming, wading, immersion, or therapeutic purposes.
Permanently Installed Swimming Pool: Those that are constructed in the ground or partially…in depth greater than 42”…weather or not served by electrical circuits…
Storable Swimming Pool: …pools intended to be stored…constructed on or above ground…maximum depth of 42”…with non-metallic walls or inflatable…
Storable
or
Permanent?

## Slide 10: 2026 National Electrical Code (NEC) Changes
Article 100 Permanently Installed Swimming Pool
Definition is revised
Pools built or installed in, on, or partially in the ground, and any pool in or on a building, regardless of any connections to electrical circuits.
Permanent

## Slide 11: 2026 National Electrical Code (NEC) Changes
Article 100 Pool
Definition is revised
Equipment designed to contain water for swimming, recreation, wading, or therapeutic use.
Info Note 1: A leisure river is a pool.
Info Note 2: Bodies of water like lakes, lagoons, surf parks, or bodies of water used for industrial purposesd are not pools. They are covered in Art 682.

## Slide 12: 2026 National Electrical Code (NEC) Changes
Squirrel
Are these the same?
Is this a pool?

## Slide 13: 2026 National Electrical Code (NEC) Changes
Article 110.16 Arc-Flash Hazard Warning Signs
Requirement revised
2023 NEC, Art 110.16: Electrical equipment, such as panelboards, industrial control panels, meter socket enclosures, and motor control centers, that is in other than dwelling units, and is likely to require examination, adjustments, servicing, or maintenance while energized shall be field or factory marked to warn qualified persons of potential arc flash hazards. The marking shall meet requirements of 110.21(B) and shall be located so as to be clearly visible to qualified persons before examination, adjustment, servicing, or maintenance of equipment.
Do you see the conflict in the 2023 code?
Field or factory marked?
110.21(B) Specific to field marking only

## Slide 14: 2026 National Electrical Code (NEC) Changes
Article 110.16 Arc-Flash Hazard Warning Signs
Requirement revised
In other than dwelling units, a permanent arc flash marking must be applied to service equipment and equipment supplied by feeders such as switchgear, switchboards, panelboards, industrial control panels, motor control centers, and meter socket enclosures if they are likely to require examination, adjustment, servicing, or maintenance while energized. The marking must be clearly visible to qualified persons and must comply with the signage requirements of 110.21(B).

## Slide 15: 2026 National Electrical Code (NEC) Changes
Article 110.16 Arc-Flash Hazard Warning Signs
Requirement revised
The label must comply with applicable industry practice and indicate the:
System voltage,
Arc flash boundary,
3. Available incident energy or minimum level of personal protective equipment (PPE) needed, and
4. Date the assessment was performed.

## Slide 16: 2026 National Electrical Code (NEC) Changes
Article 110.16 Arc-Flash Hazard Warning Signs
How do I make an arc flash assessment?
NFPA 70E, Art 130.5
(E) Arc flash boundary
and Table 130.7(C)(15)(a) Catagories for Alternating Current (ac) Systems
(F) Arc flash PPE

## Slide 17: 2026 National Electrical Code (NEC) Changes
Article 110.26 Space About Electrical Equipment
Requirement clarified for access and/or egress obstruction requirements.
2023 NEC, Art 110.26 Spaces About Electrical Equipment: Access and working space shall be provided and maintained about all electrical equipment to permit ready and safe operation and maintenance of such equipment.
2023 NEC, Art 110.26(C)(2) Open equipment doors shall not impede the entry to or egress from a working space.

## Slide 18: 2026 National Electrical Code (NEC) Changes
Article 110.26 Space About Electrical Equipment
Requirement clarified for access and/or egress obstruction requirements.
Access/egress is obstructed if one or more equipment door(s) reduces access to or egress from the working space to less than 24” wide or 6’6” high when the doors are or can be opened to 90°.
24”
6’6”

## Slide 19: 2026 National Electrical Code (NEC) Changes
Article 110.26 Space About Electrical Equipment
Requirement clarified for access and/or egress obstruction requirements.
For equipment likely to require examination, adjustment, servicing, or maintenance while energized, working space must comply with 110.26(A)(1)-(A)(4).
If special permission is granted, smaller working spaces are allowed for voltages up to 30v RMS, 42v peak, or 60v DC.
Who grants “special permission” ?
Authority Having Jurisdiction (AHJ)

## Slide 20: 2026 National Electrical Code (NEC) Changes
Article 110.26 Space About Electrical Equipment
Requirement clarified for access and/or egress obstruction requirements.
Clearance in front of equipment must comply with table 110.26(A)(1) for AC and DC voltages, unless allowed by (a) or (b). Distance is measured from the enclosure front or opening if the live parts are enclosed.
Cond 1
Cond 3
Cond 2

## Slide 21: 2026 National Electrical Code (NEC) Changes
Article 120.13 & 120.41 Dwelling Unit Calculations
Requirement revised
To understand 120.13 we need to understand 120.41 Dwelling Units: The lighting and general-purpose load calculations for dwelling units were reduced by 33%.
Dwelling units are calculated at 2vA per sqft, which includes the receptacles and lighting outlets in 120.41(1)-(3). Motors rated less than 1/8 hp are also included if connected to a lighting circuit.
What are examples motors connected to a lighting circuit?

## Slide 22: 2026 National Electrical Code (NEC) Changes
Article 120.13 & 120.41 Dwelling Unit Calculations
(1) Any 15A or 20A general-use receptacle outlets, including those in bathrooms [210.11(C)(3)] or garages [210.11(C)(4)].
(2) The outdoor, garage, accessory buildings, and basement receptacles discussed in 210.52(E) and (G).
(3) The lighting outlets included in 210.70.

## Slide 23: 2026 National Electrical Code (NEC) Changes
Article 120.13 Number of Branch Circuits for Dwelling Unit
A different calculation for minimum number of dwelling unit branch circuits was added.
Dwelling units must be calculated at 3vA per sqft when determining the minimum number of branch circuits.
1,763 sqft house
1,763 x 3vA = 5,289 vA
5,289vA/120v = 44.075A
3-15A or 2-20A and 1-10A required for lights and receptacles but…

## Slide 24: 2026 National Electrical Code (NEC) Changes
Article 120.57 Electric Vehicle Supply Equipment (EVSE)
Requirement Revised
For EVSE, the nameplate is used if available. If it is not available, an assumed load of 7,200vA is to be used.
32A x 208v = 6,656vA
32A x 240v = 7,680vA
2023 required 7,200 vA
Use Art 625 in conjunction with 120.57 to determine reduced load calculation

## Slide 25: 2026 National Electrical Code (NEC) Changes
Article 210.8 Ground-Fault Circuit-Interrupter Protection for Personnel
Clarification made and rules for HVAC revised to expand ampere rating and reduce protection req.
2023 NEC, Art 210.8 Listed GFCI protection must be provided as required in 210.8(A) through (F). The GFCI device must be in a readily accessible location.
Is the receptacle in the ceiling READILY accessible?
Readily accessible shall not resort to the use of portable ladders…
Ex: A GFCI device on a rooftop only needs to be readily accessible from the rooftop.
Allowed by
Exception

## Slide 26: 2026 National Electrical Code (NEC) Changes
Article 210.8 Ground-Fault Circuit-Interrupter Protection for Personnel
Clarification made and rules for HVAC revised to expand ampere rating and reduce protection req.
Info Note 2: See UL943 for information about GFCIs marked “HF” or “HF+” that are used in applications with high frequency leakage currents from adjustable speed drives.
Dr. Charles Dalziel Study of Electrical Shock on a Subject…

## Slide 27: 2026 National Electrical Code (NEC) Changes
Article 210.8 Ground-Fault Circuit-Interrupter Protection for Personnel
Clarification made and rules for HVAC revised to expand ampere rating and reduce protection req.
HF is designed for adjustment of the no trip threshold was added to prevent nuisance tripping.
HF+ was designed to trip the must trip threshold was not added.
Where would we typically find adjustable speed drives for the city utilities?

## Slide 28: 2026 National Electrical Code (NEC) Changes
Article 210.8(A)(2) & (3) Garages and Accessory Buildings
Clarification made and rules for HVAC revised to expand ampere rating and reduce protection req.
All 125-250v receptacles supplied by a single-phase branch circuit rated 150v or less to ground must be GFCI protected if located in the following locations:
Where would we typically find adjustable load speed drives in a dwelling?
Refrigerator
Convection
Oven
Washer
Dryer
GFCI protection is required for receptacles in garages.
Areas of accessory buildings that are not intended as habitable spaces, and used as work areas, storage areas, or similar.
Habitable
Non-Habitable

## Slide 29: 2026 National Electrical Code (NEC) Changes
Article 210.8(A) Dwelling Units
Clarification made and rules for HVAC revised to expand ampere rating and reduce protection req.
Ex 4: Factory-installed receptacles that are an internal part of a bathroom an exhaust fan do not reguire GFCI protection unless required by the listing or instructions.
i.e. if its above a tub or shower it must be marked and GFCI protected.

## Slide 30: 2026 National Electrical Code (NEC) Changes
Article 210.8(B) Other Than Dwelling Unit
Clarification made and rules for HVAC revised to expand ampere rating and reduce protection req.
All 125-250v receptacles supplied by a single-phase branch circuit rated 150v or less to ground and 50A or less; and all receptacles supplied by 3-phase branch circuits rated 150v or less to ground and 100A or less must be GFCI protected if located in the following locations:
(14) Open aquatic containers or vessels such as aquariums, bait wells, and similar if the receptacle is within 6’ of the top inside edge or rim or from any conductive surface supporting it.
Spot the difference…
Enclosed
Open

## Slide 31: 2026 National Electrical Code (NEC) Changes
Article 210.8(F) Outdoor Outlets at Dwelling Units
Clarification made and rules for HVAC revised to expand ampere rating and reduce protection req.
Outdoor outlets at dwellings, including those in the following locations, must be GFCI protected if supplied by single-phase branch circuits rated 150v or to ground and 60A or less.
September 1, 2026 NEC 210.8(F) Exception 2 is due to expire. Listed HVAC equipment supplied by an outlet covered by 210.8(F) will need an applicable GFCI or SPGFCI protection path in jurisdictions enforcing the 2026 NEC.

## Slide 32: 2026 National Electrical Code (NEC) Changes
Article 210.8(F) Outdoor Outlets at Dwellings
Clarification made and rules for HVAC revised to expand ampere rating and reduce protection req.
GFCI protection is not required for snow-melting, deicing, or pipeline/vessel heating equipment.
See 426.28 for GFPE requirements.
Garages with a floor at or below grade level.
Accessory buildings
Boathouses.
If equipment in these locations is replaced, the outlet for the equipment must be GFCI-protected.

## Slide 33: 2026 National Electrical Code (NEC) Changes
Article 210.8(F) Outdoor Outlets at Dwellings
Clarification made and rules for HVAC revised to expand ampere rating and reduce protection req.
Ex 3: Listed Class C SPGFCI is allowed for listed HVAC equipment. A warning label must be applied at disconnecting means stating “Warning: Class C SPFGFCI Protection Provided for HVAC Unit.”
Typical GFCI is class A that trip between 4 to 6mA vs.
SPGFCI trips at 20mA.

## Slide 34: 2026 National Electrical Code (NEC) Changes
Article 210.52 Dwelling Unit Receptacle Outlets
Cabinets without countertops or work surfaces was removed and receptacles located below kitchen countertops and/or work surfaces clarified.
Art 210.52 requires outlets in dwellings, in addition to any that are:
(1) Part of a luminaire or appliance.
(2) Controlled by a wall switch or a listed wall-
mounted control device.
Exhaust Fan Receptacle
Does NOT Count
(3) Located in cupboards or cabinets.
(4) More than 5’6” above the floor.

## Slide 35: 2026 National Electrical Code (NEC) Changes
Article 210.52 Dwelling Unit Receptacle Outlets
Baseboard heaters with factory installed receptacles, or separate manufactured assemblies, count as required receptacles, but they may not be on the heater circuit.
Info Note: The instructions for listed baseboard heaters might not allow for receptacles above them.

## Slide 36: 2026 National Electrical Code (NEC) Changes
Article 210.52 Dwelling Unit Receptacle Outlets
Art 210.52(A) In every kitchen, family, dining, recreation, or living room; parlor, library, den, sunroom; bedroom or similar, receptacle outlets are required in accordance with 210.52(A)(1) through (A)(5).
Art 210.52(A)(1) Spacing Receptacle outlets must be installed so that no point, measured horizontally along the floor line, is more than 6’ from a recepitacle outlet.
w/i 6’
w/i 6’
?
Is wall space 2’
Art 210.52(A)(2)(1) A wall space includes: (1) Any wall space 24” or wider and unbroken by doorways and similar, stationary appliances, fireplaces, or fixed cabinets without a countertop or similar work surface.
Is this a wall
space?
Yes if 2’ or more
and recepitacle is
less than 5’6” from
The floor.

## Slide 37: 2026 National Electrical Code (NEC) Changes
Article 210.52 Dwelling Unit Receptacle Outlets
Art 210.52(A)(2)(2) A wall space includes: The space occupied by fixed panels in walls, other than sliding panels.
What we talking about?
Fixed
Panel
Sliding
Panel
w/I 6’
w/I 6’

## Slide 38: 2026 National Electrical Code (NEC) Changes
Squirrel
Is this a wall space?

## Slide 39: 2026 National Electrical Code (NEC) Changes
Article 210.52 Dwelling Unit Receptacle Outlets
Art 210.52(A)(2)(3) A wall space includes: The space created by fixed dividers, such as free-standing bars or open railings.
If over 6’ the requirement
Can be satisfied with a floor
receptacle.

## Slide 40: 2026 National Electrical Code (NEC) Changes
Article 210.52(A)(5) Prohibited Locations

## Slide 41: 2026 National Electrical Code (NEC) Changes
Article 210.52(A)(5) Prohibited Locations
For receptacles installed at free-standing bars [210.52(A)(2)(3)], receptacles may not be below the countertop or work surface if they are within 24” of the countertop or work surface.
Art 210.52(C)(2) Islands and peninsulas: If a receptacle is installed to serve a countertop or work surface of an island or peninsula, it must comply with 210.52(C)(3) and (C)(4).

## Slide 42: 2026 National Electrical Code (NEC) Changes
Article 210.52(C)(2) Islands and Peninsulas
If an outlet is not installed, electrical provisions to add one in the future must be provided at the island or peninsula.

## Slide 43: 2026 National Electrical Code (NEC) Changes
Article 210.52(C)(3) Location
Receptacle outlets must be in one of the following locations:
(1) On or up to 20” above the countertop or work surface.
(2) Receptacle outlet assemblies listed for use in countertops may be installed in countertop or work surface areas.
…must be listed for countertop (32oz spill test) not work surface (8oz spill test).
(3) Receptacle outlet assemblies listed for use in countertops or work surfaces may be installed in work surfaces.

## Slide 44: 2026 National Electrical Code (NEC) Changes
Article 210.52(C)(3) Location
Receptacle outlets must be in one of the following locations:
Receptacles that are not readily accessible due to appliances fastened in place, appliance garages, sinks, or appliances occupying assigned space do not count as the receptacle outlets required by 210.52(C)(3).

## Slide 45: 2026 National Electrical Code (NEC) Changes
Article 210.52(C)(4) Prohibited Location
Receptacles, including non-required receptacles, that are accessible outside of a cabinet or wall surface and are below a countertop or work surface are not allowed in either of these locations:
(1) Not allowed on an adjacent wall within 24” from the cabinet.
(2) Not allowed within 24” of the countertop or work surface.
24”
24”
Ex: Receptacles in a drawer are allowed beneath a countertop or work surface.

## Slide 46: 2026 National Electrical Code (NEC) Changes
Article 210.63 Equipment Requiring Servicing
Receptacle requirement clarified.
A 15A or 20A, 125v receptacle outlet is required within 25’ of the equipment specified in (A) and (B).
Don’t forget a maintenance receptacle
For mini-split installations…
Anything else?
2024 IMC 1101.3 Refrigeration
line protection?
Art 210.63(B) Other Electrical Equipment: Within other than dwelling units, a receptacle outlet must be provided for wiring systems that include a solidly grounded system operating at less than 150v to ground.
Not located within…
The receptacle must be located in the same area as indoor panelboards, switchboards, switchgear, service equipment, and motor control centers.

## Slide 47: 2026 National Electrical Code (NEC) Changes
Article 210.70 Required Lighting Outlets
Laundry lighting clarified
Lighting outlets must be provided in accordance with 210.70(A)-(C).
210.70(A) In dwelling units, lighting outlets are required in accordance with 210.70(A)(1) and (A)(2).
210.70(A)(1) At least one lighting outlet controlled by a listed wall-mounted control device or switch must be provided in habitable rooms, kitchens, bathrooms, and laundry areas.
Switches or wall mounted control devices must not rely on a battery unless loss of battery power energizes the lighting outlet.

## Slide 48: 2026 National Electrical Code (NEC) Changes
Art 210-70(A)(1) The control device or switch must be located near an entrance to the room.
Ex 1: In other than kitchens, laundry areas, and bathrooms, receptacles controlled by a listed wall-mounted device or switch are allowed instead of lighting outlets.
Ex 2: Occupancy sensors installed at a customary wall switch location may control the lighting outlets if they have a manual override setting.
Ex 3: For laundry areas, the illumination and its control may be located outside of the laundry area if the laundry equipment is in a closet.

## Slide 49: 2026 National Electrical Code (NEC) Changes
Article 225.31 Building Disconnect Means
(Talking about feeders 230 is service disconnect)
The building disconnecting means no longer required to be in or on the building.
Art 225.31(A) A disconnect is required for all ungrounded conductors that enter a building. If the building disconnect also serves as the emergency disconnect for a dwelling, it must compy with 225.41.
Art 225.31(B) Location: The building or structure disconnect must be readily accessible and, if inside the building, located where the conductors enter the building. The allowances of 230.6 may be used for this application. If located outside the building, it must be within sight of the building.
Within 50’ and within sight
Over 50’

## Slide 50: 2026 National Electrical Code (NEC) Changes
Hazards of an electrical inspection…

## Slide 51: 2026 National Electrical Code (NEC) Changes
Art 225.31(B) Location
Ex 1: If documented procedures exist, the installation is monitored by qualified persons, and is under single management, the disconnect may be elsewhere.
Ex 2: For installations that could have increased hazards if unexpected power loss occurs, the disconnect may be elsewhere.
Ex 3: Towers and poles for lighting may have their disconnecting means located elsewhere.
Ex 4: Poles and similar that support electric signs must comply with 600.6 for disconnecting means.

## Slide 52: 2026 National Electrical Code (NEC) Changes
Article 230.67 Surge Protection
Locations added to 215.18 feeders and 230.67 services
Art 230.67(A) An SPD is required for services supplying:
(1) Dwelling units,
(2) Dormitories units,
(3) Guest rooms and guest suites of hotels, motels, and dormitories,
(4) Patient sleeping rooms of nursing homes and limited care facilities, and
(5) Sleeping quarters of police, rescue, ranger, ambulance, or fire stations, and similar locations.

## Slide 53: 2026 National Electrical Code (NEC) Changes
Art 230.67(B) The SPD must be part of the or adjacent to the service equipment.
Ex: An SPD is not required at the service if the service supplies only feeders and an SPD is provided at the load side of each feeder.
Not required here if
the panelboard it
serves has an SPD.

## Slide 54: 2026 National Electrical Code (NEC) Changes
Article 230.70 General (Service Equipment)
One & two-family service must be outdoors and 230.85 emergency disconnect removed.
Art 230.67(A) An SPD is required for services supplying:
A way to disconnect the ungrounded service conductors from the building or structure must be provided.

## Slide 55: 2026 National Electrical Code (NEC) Changes
Art 230.70(A)(1) Dwelling Units: The service disconnect must be outdoors and readily accessible, and be located either
(1) On the dwelling unit, or
(2) Within sight of the dwelling unit.
Ex: The service disconnect does not need to be within sight if an emergency disconnect complying with 225.41 is installed.
Within 50’ and within sight
Over 50’
Nees an emergency
disconnect
Remote control devices are not service disconnects.

## Slide 56: 2026 National Electrical Code (NEC) Changes
Article 240.24 Location in/on premises (OCPD)
Panelboard in existing bathrooms added.
Art 240.24(E) Not in bathrooms: Overcurrent protective devices (other than supplementary devices) are not allowed in bathrooms, showering facilities, or locker rooms.
Bet the glass isn’t tempered either…
Ex: Installing an OCPD in an existing panelboard in a bathroom is allowed if the panelboard was installed before this requirement was added.
Does not address in a existing stairway
but the same rule can be reasonably
applied by the AHJ.

## Slide 57: 2026 National Electrical Code (NEC) Changes
Article 250.8 Grounding and Bonding Connections.
Section revised
Only methods indicated in 250.8(A) are allowed for connecting equipment grounding conductors, grounding electrode conductors, bonding jumpers, or grounding and bonding terminations.
What else is needed?
GEC >6awg and exposed to damage or <6awg, exposed to damage or not must be in conduit and secured (250.64(A))

## Slide 58: 2026 National Electrical Code (NEC) Changes
Article 250.64 Grounding Electrode Conductor Installation.
Splicing option added & enclosure holes addressed.
Art 260.64(C) The grounding electrode conductor is not allowed to be spliced, unless the splice is made with any of these methods:
(2) Listed grounding and bonding equipment for accessible splices of wire-type GECs.
Listed wire connector only
Listed for grounding & bonding.
Art 260.64(G) A GEC may not be installed through any ventilation, drainage, or mounting opening in an enclosure.
Drain hole.
Knockout.

## Slide 59: Air Barriers

## Slide 61
https://codes.iccsafe.org/content/IRC2024V2.0/chapter-11-re-energy-efficiency#IRC2024V2.0_Pt04_Ch11_SecN1102.5.1.1_TblN1102.5.1.1
Notes: Click link to 2024 IRC AIR BARRIER, AIR SEALING AND INSULATION INSTALLATION
Air Barrier
Seal backside of receptacles and penetrations for airtight barrier, note this is for walls and ceilings between the thermal envelope only.

## Slide 62
Notes: Click link to 2024 IRC AIR BARRIER, AIR SEALING AND INSULATION INSTALLATION
Air Barrier
Seal backside of receptacles and penetrations for airtight barrier, note this is for walls and ceilings between the thermal envelope only.

## Slide 63
Notes: Air Barrier
Seal backside of receptacles and penetrations for airtight barrier, note this is for walls and ceilings between the thermal envelope only.

## Slide 64
Notes: Air Barrier
Seal backside of receptacles and penetrations for airtight barrier, note this is for walls and ceilings between the thermal envelope only.